## MetBAM Checklist South
KCBX TERMINALS CO SOUTH |  | SITE VISIT DATE
| 2018-05-01 | 2018-05-04 | 2018-05-11 | 2018-05-18 | 2018-05-22 | 2018-05-25 | 2018-05-29
Meteorological Station
Arrival time: | 9:15 | 9:20 | 12:15 | 8:45 | 9:50 | 8:35 | 9:10
Is the temperature aspirator fan running? | bar: 2018-05-01 to 2018-05-29
Are all signal cables secured and intact? | bar: 2018-05-01 to 2018-05-29
Are wind vane/ anemometer cups intact and operational? | bar: 2018-05-01 to 2018-05-29
Is datalogger date/time correct within 60 sec? | bar: 2018-05-01 to 2018-05-29
Are conditions shown on logger consistent with ambient observations? | bar: 2018-05-01 to 2018-05-29
BAM-1020 PM10 Monitors
Arrival time: | 9:15 | 9:20 | 12:15 | 8:45 | 9:50 | 8:35 | 9:10
Any status error flags showing? | bar: 2018-05-01 to 2018-05-29
Are all monitor dates/times correct within 60 sec? | bar: 2018-05-01 to 2018-05-29
Are all filter transport systems operational? | bar: 2018-05-01 to 2018-05-29
Are all tape reel cover knobs secure? | bar: 2018-05-01 to 2018-05-29
Are hourly data being collected? | bar: 2018-05-01 to 2018-05-29
Is sampler inlet and downtube clean? | bar: 2018-05-01 to 2018-05-29
Is water collection bottle clean? | bar: 2018-05-01 to 2018-05-29
Are O-rings in good condition? | bar: 2018-05-01 to 2018-05-29
Comments section
5/1, Changed time on the ST-NW BAM from 09:23:10 to 09:22 CST.
5/11, Performed BAM QC checks.
5/18, Change time on the ST-N BAM from 08:55:55 to 08:57 CST.
5/18, Changed out WS sensor.
5/25, Performed BAM QC checks.
5/29, Changed time on the ST-NE BAM from 09:49:10 to 09:48 CST.
Site ID List: | 2018-05-04: MAINTENANCE LIST FOR METEOROLOGICAL STATION
ST-NW = Northwest BAM site | 2018-05-04: Each Visit:; 2018-05-11: Inspect sensors and cables for signs of deterioration or damage and replace as needed
ST-N = North BAM site | 2018-05-04: Monthly:; 2018-05-11: Inspect temperature aspirator and remove dust accumulation
ST-NE = Northeast BAM site (Partisol samplers) | 2018-05-11: Inspect tower for plumb, and verify that all fasteners are intact and tight
ST-M = Meteorological Monitoring Site | 2018-05-04: Biannually:; 2018-05-11: Perform calibration check on sensors
ST-CE = Center East BAM site | 2018-05-11: Check wind sensor bearings
ST-SW = Southwest BAM site | 2018-05-04: Annually:; 2018-05-11: Replace wind sensor bearings
MAINTENANCE LIST FOR BAM-1020
|  | Each Visit: | Inspect filter tape and replace when needed (~2 months/roll; run SELF-TEST function in the TAPE menu).
Inspect filter tape for pinholes and irregular PM deposits
|  | Monthly: | Perform flow rate and leak check
Clean BAM nozzle and vane
Clean inlet hardware, capstan shaft and pinch roller
|  | Quarterly: | Verify BAM settings file
Flow system calibration
Disassemble and clean inlet
|  | Biannually: | Check pump muffler and tubing and replace as needed
Test filter RH and Temperature sensors
Test smart heater function
|  | Annually: | Perform zero background test
Clean internal debris filter
Remove and check membrane span foil
Beta detector count rate and dark count test
Rebuild vacuum pump
Replace nozzle o-ring